## 1" x 5¦8" Manifold Calculator
1" manifold suppy/return ports & header pipe
Feeder/Manifold | L (distance to manifold): | 50 | ft | Flow velocity:
| ΔT (intended temp drop of system): | 5 | °F | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Tin (temp of fluid entering circuit): | 100 | °F | 15.5718 | f/s | 9.9659 | f/s | 6.9208 | f/s | 3.8929 | f/s
| Percent fluid mixture water (1.0): | 100 | %
| H (head pressure maintained by circulator): | 9 | ft | Head Loss per foot:
| Hzone (head pressure avaiable to zones): | 3.1726 |  | 2.1215 | ft | 0.79543 | ft | 0.38335 | ft | 0.11655 | ft
| fdemand (demanded flow of system): | 9.5415 | GPM
| Q (total heat load of system): | 24078.7165 | Btu/hr | Pipe c values from Figure 6-28, page 210
| Percent fluid mixture methanol (.75): | 0 | % | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| c (Specific heat of fluid): | 1 | Btu/lb./°F | 0.786 | c | 0.2947 | c | 0.14203 | c | 0.04318 | c
| D (Density of liquid): | 61.9686 | lb./ft.3
| Dynamic Viscosity: | 0.0004568 | lbm./ft./sec. | Flow estimation:
| a: | 0.052106 |  | ΔT: |  |  | 5 |  | °F
| Re (equivalent hydrolic resistances of zones): | 0.059537 |  | Btu dissipation: |  |  | 24000 |  | Btu
| Rh (equivalent hydrolic resistances of header): | 0.1125 |  | f (Flow Rate): |  |  | 9.6702 |  | GPM
.
5/8" manifold ports & pipe
Zone 1 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756 | ft
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 2 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756 | ft
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 3 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 4 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 5 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 6 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 7 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 8 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 9 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 10 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 11 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 12 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 2006.5597 | Btu/hr | 1.3195 | f/s | 0.84446 | f/s | 0.58643 | f/s | 0.32987 | f/s
| fzone (flow of zone): | 0.8085 | GPM
| rzone (hydrolic resistance of zone): | 4.6067 |  |  |  | TRUE
| HLzone (head loss of zone): | 3.1756
| rbalance (manually added hydrolic resistance of zone): | 0

## 3¦4" x 1¦2" Manifold Calculator
3/4" manifold suppy/return ports & header pipe
Feeder/Manifold | L (distance to manifold): | 50 | ft | Flow velocity:
| ΔT (intended temp drop of system): | 5 | °F | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Tin (temp of fluid entering circuit): | 100 | °F | 8.2102 | f/s | 5.2545 | f/s | 3.649 | f/s | 2.0526 | f/s
| Percent fluid mixture water (1.0): | 100 | %
| H (head pressure maintained by circulator): | 9 | ft | Head Loss per foot:
| Hzone (head pressure avaiable to zones): | 2.7469 |  | 0.6921 | ft | 0.25949 | ft | 0.12506 | ft | 0.038022 | ft
| fdemand (demanded flow of system): | 5.0308 | GPM
| Q (total heat load of system): | 12679.8937 | Btu/hr | Pipe c values from Figure 6-28, page 210
| Percent fluid mixture methanol (.75): | 0 | % | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| c (Specific heat of fluid): | 1 | Btu/lb./°F | 0.786 | c | 0.2947 | c | 0.14203 | c | 0.04318 | c
| D (Density of liquid): | 61.9686 | lb./ft.3
| Dynamic Viscosity: | 0.0004568 | lbm./ft./sec. | Flow estimation:
| a: | 0.052106 |  | ΔT: |  |  | 5 |  | °F
| Re (equivalent hydrolic resistances of zones): | 0.15879 |  | Btu dissipation: |  |  | 24000 |  | Btu
| Rh (equivalent hydrolic resistances of header): | 0.37003 |  | f (Flow Rate): |  |  | 9.6702 |  | GPM
.
1/2" manifold ports & pipe
Zone 1 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572 | ft
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 2 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572 | ft
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 3 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 4 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 5 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 6 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 7 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 8 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 9 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 10 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 11 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0
Zone 12 | Lzone (loop distance of zone): | 300 | ft | 0.5 | " | 0.625 | " | 0.75 | " | 1 | "
| Qzone (heat dissipation of zone): | 1056.6578 | Btu/hr | 0.69483 | f/s | 0.44469 | f/s | 0.30881 | f/s | 0.17371 | f/s
| fzone (flow of zone): | 0.42576 | GPM
| rzone (hydrolic resistance of zone): | 12.2866 |  |  |  | TRUE
| HLzone (head loss of zone): | 2.7572
| rbalance (manually added hydrolic resistance of zone): | 0